Wireless Energy meter Using GSM Technology

Sanjay M. Koli

Assistant Professor, Electronics and Telecommunications Department,

Vishwakarma Institute of  Information Technology,

Kondwa (Bk), Pune-411 048, Maharashtra, India.

Email: sanjaykoli@yahoo.com

Abstract — The paper discusses the design and testing of a prototype wireless energy meter with the help of widely spread GSM network. The energy consumed by a load of 400W, 600W and 800W was calculated by the energy meter and send through the mobile unit via short messageing services (SMS) to the remote mobile unit of an elecrticity distribution company using existing GSM technology. The measurements were compared with the conventional energy meter and found promising with good accuracy. The necessary circuits for displaying the consumed energy and interfacing were also done at the transmitter side.

Key words: Energy meter, GSM technology, automatic meter reading, automatic polling mechanism

1. INTRODUCTION

In this modern era of technology the conventional systems used in every walks of the life have been replaced by the new once. The changing technology has replaced the electro-mechanical energy meters with the digital wireless energy meters. So, that the energy distribution personals could access these meters form the remote location with the help of the vastly deployed GSM Services.  This will definitely offer a great convenience to the meter reading task and also speed up the process of billing with full accuracy, as it reduces the human reading errors.  Also, it permits for automated billing process.  Hence, an effective as wel as efficient energy management could be done for a large number of distributed subscribers. The centralized data collection system  could collect the energy consumption readings from the energy meters wirelessly using automatic meter reading and the automatic polling mechanism. Thus human intervention could be reduced to improve the energy management.

Advancements in the communication technology  has to be used to solve the common problems in the human life. Seeing to the limitations and social aspects of  building new power generating stations, it has become mandatory to plan and use efficiently the existing ones. The digital wireless energy meter using GSM Technology [1], that the author have designed and successfully implemented, is superior to its electro-mechanical predesessors in terms of accuracy, billing, temper –detection capabilities, flexibility, manufacturability, reliability, feature –set and cost.

Automatic meter reading helps to the consumer, to the energy generating company, to the energy distrubution company by giving access to the latest and accurate information from the metering devices. This in-turn saves time, manpower and helps for an efficient energy management as wel as energy tracking. As the network of mobile is getting  rapidly and widely spread to each and every point with  the reduced cost, the author have used it for effective as wel       as

efficient energy management.The  system have been designed to meet objectives: viz.,

- Basic functionalities of conventional meters

- Capability to store the readings over a period of time

- Various power factors (1, 0.5 lead, 0.5 lag)

- Interlinking of energy meter with GSM

2. THE SYSTEM DESIGN

The block diagram schematic of the system is as shown in the Fig. 1. It consists of three main distinctive stages. The first stage consists of the interface between active energy metering circuit and microcontroller. The second stage comprises   of   interface   between   liquid crystal display (LCD), real time clock (RTC)  with microcontroller. The third stage consists of interfacing between digital wireless energy meter and mobile unit or module.

2.1 Functional description of the blocks

The digital wireless energy meter has two primary input sensing circuits, one for current sensing and the second for voltage sensing. The active energy metering circuit senses the current and voltage to calculate the energy consumed. The electrical power is the product of the voltage and current waveforms. The resulting waveform is called the instantanteneous power signal and it is equal to the rate of energy flow at every instant of time. The active power is equal to the dc component of the instantanteneous power signal given by equation (1) and is used to calculate active power in the ADE7756.

The DC component of the instantanteneous power signal is extracted by low pass filter to obtain the active power information. The process is graphically illustrated in Fig. 2.

2.1.1 Energy Calculation

The consumed energy ‘E’ of any given load during a time interval [3] (t (=t2 – t1) is given by equation (2)

The   ADE7756   achieves   the   integration  of  the

active power signal by continuously accumulating  the active power signal. While calculating the energy, this integration removes the sinusoidal components present, if any, that may be in the active power signal. The microcontoller processes, stores the energy consumption and also controls all the units for synchronous operation. It initiates all the processes like receiving the input data and sending the data through the GSM link to the dedicated mobile of the system.

The energy consumption is indicated by 16 x 2 LCD  display; which is capabale of displaying two lines, each of 16 characters. The RTC DS1307 used gives the liveness to the Energy meter for sending the data to the electricity distribution company. Also it contains calender alongwith clock plus 56 bytes of nonvolatile static RAM (SRAM). The DS1307 address and data are transferred serially via a 2 wire bi-directional bus with the microcontroller.

The serial port is interfaced to the microcontroller by using the serial IC DS232A. It provides easy interface of the serial port to the microcontroller. The GSM mobile/module is used  for sending the usage of the energy consumed through short messaging services (SMS) to the electricity distribution company. The bill for the consumption will be send via the mobile unit at the electricity distribution company to the subcribers mobile/module.

Fig. 1: Block Diagram of the system

2.1.2 Design of the hardware

The hardware for this wireless energy meter is designed and developed and involves

A) Design of analog section

- Power meter using input sensors potential transformer (PT) and current transformers (CT)

B) Design of digital section

- Design of active energy metering circuit usingADE7756

- Interfacing of RTC DS 1307 with microcontroller

- Interfacing of LCD display JHD 162A with microcontroller

- Interfacing of DS232 with microcontroller

- Interfacing of GSM mobile/module unit  with microcontroller.

2.2  Design considerations for input sensors

This energy meter is designed for single-phase power supply and the maximum current value is 10 A. The high magniude current and voltage signals of the mains supply must be brought down to lower level for easy process.This is done by using sensors/transducers called PT and CT, which are being used as sensors.

Fig. 2: Active power calculation

A) Design of potential transformer(PT)

The specifications for PT used in this meter are

i) Maximum primary voltage – 250 Vrms,

ii) Corresponding secondary voltage – 9 Vrms.

The potential transformer is connected in parallel of the   load so as to sense the potential. This high potential is   steped down to 9V using transformer.

B) Design of current transformer (CT)

The specifications for MS steel core CT used in this meter are

i) Maximum primary current            – 5 A (rms)

ii) Corresponding secondary current –  50  mA.

The output current of CT is converted to the corresponding proportionate voltage for the purpose of measusrment as shown in the Fig. 3. By connecting a 200 (, 2W replica resistance across secondary terminals of CT  (5A: 50mA) will create a maximum voltage drop of 50mA x 200 ( = 10 V rms at the secondary at maximum rated loading. The current transformer converts 5A current to 50 mA and 9V.

C) Design

Transformer rating = 9V.

Current drawn        = 50 mA.

Therefore, the resistance value required = 9/50mA=   180(.

Hence, selected  value of resistance is 200( and connected across the secondary coil of the current transformer.

2.3 Design of active energy metering circuit

The ADE7756 is available in 20-lead dual in line (DIP) package. It is a high-accuracy electrical power measurement IC with a serial interface and pulse output. It incorporates two second order sigma-delta analog to digital convertors (ADC), reference circuitry, temperature sensor and all the signal processing required to perform active power and energy measurement. The circuit arrangement is  shown     in

Fig. 3: Circuit for Conversion of  current to voltage

Fig. 4.

The instanteneous power is given by equation (1). The average power over an integral number of cycles (n) is given by equation (3).

where, T is the line cycle period and P is referred to as the active or real power. This active power is equal to the DC component of the instantaneous power signal in equation (1). This DC component is extracted by low pass filter (LPF) to obtain the active power information. This signal processing chain of the active power calculation in ADE7756 is as shown in the Fig. 5.

Due to instanteneous power signal some ripples are present in the active power signal.This ripple is sinusoidal and has a frequency equal to twice the line frequency. Since the ripple is sinusoidal in nature, it will be removed when the active power signal is integrated to calculate energy. The ADE7756 achieves the integration of the active power signal by continuous accumulation of the active power signal.

2.4 Energy meter display

The energy meter displays the energy consumed in KWh unit. All ADE7756 functionality is accessible via several on-chip registers.The contents of these registers could be updated or read using the on-chip serial interface. Each register is accessed by first writing to the communications register and then transfering the register data.

2.5  Design considerations of degital section

The digital card consists of the 8 bit microcontroller 89c51, interfacing of ADE7756, RTC DS1307 and LCD display JHD 162A with microcontroller.

Microcontroller card design:

2.5.1 Interfacing ADE7756 with microcontoller

Table I given below shows the connection details.

TABLE 1:PINS TO BE CONNECTED

| Pin numbers of ADE7756 | Pin numbers of 89c51 |
| --- | --- |
| 17 | 1 |
| 18 | 2 |
| 19 | 3 |
| 20 | 4 |

Fig. 4: Circuit diagram for calculating energy

Fig. 5: Signal  processing chain of the active power

2.5.2 Crystal Interfacing

The 89c51 has on chip oscillator[2]. Hence across pin number 18 and 19, we interface piezoelectric crystal of frequency 11.059 MHz/12mV. The author have selected 11.059 MHz because it is easier to select baud rate of 9600 bps for the serial communication with GSM mobile /module. The selection of baud rate is explained further in the paper.

2.5.3 Reset circuitry

The reset circuitary (RC) (differentiator circuit) is used as power ON reset circuitry and connected at pin 9 of microcontroller. This reset is active high and should be hold high for 24 clock oscillator period. Thumb rule for selection of capacitor is in the range- 1(f to 10 (f and for resister in the range -1K( to 10 K(. The author have selected 5.6 K( and 10 (f.

2.5.4 LCD module interface

The LCD module of Orion JHD 162A is used in the Energy Meter. The interfacing details with the microcontroller is shown in Fig. 6.

Fig. 6: LCD Interfacing

2.5.5 Real time clock  interface

The DS1307 is serial real time clock with a low-power, full BCD clock/calender plus 56 bytes of non-volatile SRAM; connected directly to one of the I/O ports on microcontroller. The interfacing of RTC with microcontroller is as shown in Fig. 7.

2.5.6 Serial communication

The GSM mobile/module could be interfaced to microcontroller  through  serial port and RS232. DS232A is a dual RS-232 driver/receiver pair which generates RS -232 voltage levels from a single +5 volt power supply. Interfacing of mobile with microcontroller using DS232A is a shown in Fig. 8. The serial port is operating in a full duplex mode. The receiver and transmitter register are both accessed at serial buffer (SBUF). The serial port supports four modes; viz,

- Mode 0: shift resister

- Mode 1: 8 bit universal asynchronous receive transmit (UART)

- Mode 2: 9 bit UART with fixed baud rate

- Mode 3: 9 bit UART with variable baud rate

2.5.6.1  Calculation of Baud rate

In Mode 1, baud rate is be obtained by,

Where, serial port mode (SMOD)=0, fosc=11.059 MHz, TH1=FD H. Hence, the Baud rate=9600 bps.

Fig. 7: Inerfacing of RTC 1307 with microcontroller

2.5.6.2  Transmit and receive routines of the energy meter

A)Transmit routine

TI flag should be checked before data is passed on to the serial buffer. TI bit or flag is in SCON register.

TI = 0 {Transmitter busy};  TI = 1 {Transmitter free}

STEPS:

i)Load data

ii)Is transmitter ready?

iii)If yes Go to steps 2. If not, then move data to    SBUF.

B)Receive routine

RI flag should be checked before receiving data. RI bit or flag is in serial port control (SCON) register.

STEPS:

i)   Data received ?

ii)  JZ No_RCV

iii) If yes-read the data. If not, then go back.

2.5.7 Interfacing GSM mobile/module with energy meter

The GSM mobile/module is connected to the communication port of the energy meter through the standard cable that comes with the mobile/module for interfacing with personal computer (PC).

Fig. 8: Interfacing of mobile with microcontroller using DS232A

The mobile/module should be capable of operating in both the protocol data unit (PDU) and the text mode. The text mode is used for this energy meter SMS operations. The attention (AT) commands  are used for the purpose of communication with the mobile. It is necessary to use a mobile/module which is GSM AT compliant. The mobile/module could be controlled in different ways by the microcontroller with the help of AT commands. Some simple AT commands for doing the SMS are,

AT+CMGR - Read message

AT+CMGS -  Send message

Text mode SMS are also available on GSM module.

2.5.8 Main routine

The main routine of the energy meter is given in Fig. 8.

Fig. 8: flowchart for main routine

3. Observations

The energy meter circuit voltages measured for the loads of 400W, 600W and 800W for unity power factor, 0.5 lead and 0.5 lag are presented in table 2 through 4. Similarly, their percentage error calculated for the above loads are given in table 5 through 7.

TABLE 2

UNITY POWER FACTOR

| Load (W) | Load Current (A) | PT output (V) | CT output (Volts) | Wattmeter Readout (Watt) |
| --- | --- | --- | --- | --- |
| 400 | 1.5 | 9.2 | 8.4 | 340 |
| 600 | 2.25 | 9.2 | 12.4 | 480 |
| 800 | 3.0 | 9.2 | 17.0 | 660 |

Table 3

0.5 lead power factor

| Load (W) | Load Current (A) | PT output (V) | CT output (Volts) | Wattmeter Readout (Watt) |
| --- | --- | --- | --- | --- |
| 400 | 1.5 | 9.2 | 8.4 | 160 |
| 600 | 2.25 | 9.2 | 12.4 | 240 |
| 800 | 3.0 | 9.2 | 18.0 | 350 |

TABLE 4

0.5 LAG POWER FACTOR

| Load (W) | Load Current (A) | PT output (V) | CT output (Volts) | Wattmeter Readout (Watt) |
| --- | --- | --- | --- | --- |
| 400 | 1.5 | 9.2 | 10.6 | 160 |
| 600 | 2.25 | 9.2 | 12.4 | 240 |
| 800 | 3.0 | 9.2 | 17.0 | 350 |

TABLE 5

ERROR CALCULATION FOR UNITY POWER FACTOR

| Load (W) | Load Current (A) | Readouts (W) | % error |
| --- | --- | --- | --- |
|  |  | GSM EM | Watt meter |  |
| 400 | 1.5 | 322 | 340 | -5.5% |
| 600 | 2.25 | 506 | 480 | 5.13% |
| 800 | 3.0 | 644 | 660 | -2.42% |

TABLE 6

ERROR CALCULATION FOR 0.5 lead POWER FACTOR

| Load (W) | Load Current (A) | Readouts (W) | % error |
| --- | --- | --- | --- |
|  |  | GSM EM | Watt meter |  |
| 400 | 1.5 | 182.1 | 160 | 12.0% |
| 600 | 2.25 | 248.4 | 240 | 3.22% |
| 800 | 3.0 | 397.4 | 350 | 11.8% |

TABLE 7

ERROR CALCULATION FOR 0.5 lAG POWER FACTOR

| Load (W) | Load Current (A) | Readouts (W) | % error |
| --- | --- | --- | --- |
|  |  | GSM EM | Watt meter |  |
| 400 | 1.5 | 198.7 | 160 | 19% |
| 600 | 2.25 | 264.9 | 240 | 9.0% |
| 800 | 3.0 | 363.3 | 350 | 3.5% |

4. APPLICATIONS AT A GLANCE

1) To monitor the energy usage in different departments of factory. This will allow us to monitor, such as the department which is using maximum power and how it could be reduced.

2) To monitor total energy usage of a small scale industry, office or residential,

3) To monitor power consumption in hazardous environment as it is difficult for the human personal to reach out these locations.

4) To monitor the power utilization in remote areas. The report or billing could be sent through SMS for the speedy access to the consumers.

5. FUTURE MODIFICATIONS

1) The system could be modified for three phase supply with the use of three current transformers and three potential transformers to calculate the total consumed energy.

2) The system also could be modified to monitor power factor, maximum demand of power in the company and its future need.

3) The system indication for crossing the upper and lower preset limit of power factor and maximum KVA demand could be made. This will help to switch ON or switch OFF necessary capacitor banks/inductive loads to correct power factor and to switch ON or switch OFF some of the loads for load shedding.

4) The system could also be modified to detect any intentional or unintentional tampering such as wrong connections, wrong phase sequence, lowering the speed etc. by the consumer.

5) The concept of prepaid energy services similar to the mobile services could be effectively implemented, where, the user has to purchase energy in advance. The users could be provided smart cards such as used in mobile, where units of consumption could be filled from anywhere.

6) The disconnection or reconnection could be done by the operator remotely from the office of the distribution company in case the client fails to pay the bills.

6. CONCLUSION

The design and testing of the wireless energy meter using GSM technology has been carried out. Necessary interfacing for the prototype model was done. The author has carried out the work with the Sony Ericsson and Nokia handsets as transmitting and receiving ends respectively. The energy consumed by various loads connected across the energy meter was sent through the SMS to the receiver mobile. The same was physically compared with the standard energy meter readings simultaneously and found that the readings of GSM based energy meter offers less error. Therefore, it is concluded that, the designed system is effective and accurate.

7. References

[1]  Joschen Schiller, “Mobile communication,” Pearson

Education (Singapore), 2004, pp 1-67, 303-346, 356-399.

[2]	 Bhupendre Singh Chhabra, “Microcontroller and its      applications”, Dhanpat Rai and Co. Ltd., 1999, pp 1-88.

[3] P. A. V. Loss, et al, “A single phase microcontroller      based energy meter,” presented at IEEE Instrumentation and Measuremnt Technology Conference, St. Paul, Minessota, USA, May 18-21, 1998, pp.797-800.

[4] B. S. Koay, et al,  "Design and Implementation of      Bluetooth Energy Meter," in Proc. of the Intl. Conf. ICICS-PCM 2003, Singapore, pp. 1474-1477, June 1993.

[5] Radwan Tahboub and Vasile Lazarescu, “Novel approach

for remote energy meter reading using mobile agents,” in Proc. of the Third Intl. Conf. on Information       Technolog:New Generations, 2006.